## Sheet1
ESD and PSS system Analysis Summary Report
| APPLICABLE TO SITES | [7 empty] | PO/OSF/ICS
Equipment / Package Class:
ESD and PSS (ESD1, SD2, SD3)
| Sites: | [12 empty] | FALSE
SNB & SNPS
FINDINGS & RESULTS FROM ANALYSIS
| Sites | Equipment / Package | Current Package PM Test Interval | Instrument Type | Current Instr PM Test Interval | Current Probability Failure on Demand Average | SIL class - current ESD1 Test Interval (Baseline 1Y) | Forecast SIL class at 2Y ESD1 test Interval | Compliance of SIL at forecast 2Y ESD1 test interval | Proposed Package PM Test Interval | Reliability | Availability | Actual ESD1 Test Validity Taken Into Account
| BKP BP1/PP | ESD1 BKP BP1/PP | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0.0025 | SIL-2 | SIL-2 | Compliant | 2Y | 99.75% | 100% | Valid
| BKP BA | ESD1 BKP BA | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0 | SIL-3 | SIL-3 | Compliant | 2Y | 100% | 100% | Valid
| BKP BB | ESD1 BKP BB | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0 | SIL-3 | SIL-3 | Compliant | 2Y | 100% | 100% | Valid
| BKP BE | ESD1 BKP BE | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0 | SIL-3 | SIL-3 | Compliant | 2Y | 100% | 100% | Valid before 1Y PRESERV
| BKP BF | ESD1 BKP BF | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0 | SIL-3 | SIL-3 | Compliant | 2Y | 100% | 100% | Valid before 1Y PRESERV
| BKP BG | ESD1 BKP BG | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0.0038462 | SIL-2 | SIL-2 | Compliant | 2Y | 99.62% | 100% | Valid
| BKP BH | ESD1 BKP BH | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0 | SIL-3 | SIL-3 | Compliant | 2Y | 100% | 100% | Valid
| BKP BJ | ESD1 BKP BJ | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0.0037037 | SIL-2 | SIL-1 | PRSERVATION | N/A | 99.63% | 100% | Valid
| BKP BL | ESD1 BKP BK | 1Y | ESD & PSS LOOP | 3M/6M/1Y | 0 | SIL-3 | SIL-3 | Compliant | 2Y | 100% | 100% | Valid
FINAL CONCLUSION(S)
1 | The extension of ESD1 yearly test to 2Y is recommended in SNB and SNPS
2 | After implementing the 2Y ESD1 test strategy it is of the utmost importance to review/analyse the result of critical SDV & ESD1 test periodically (i.e. Annually) in order to verify if SIL level is still maintained!
3 | The current 1Y ESD1 test interval is based on MHK-COMP-SPE-EP-SAF-0371. An approval on the Derogation request is required to implement the 2Y-ESD1 test strategy for each recommended SNB area and SNPS
FOLLOW UP FROM ANALYSIS
A | Valve/actuator with poor availability will be replaced / refurbished by ensuring and securing the procedures for repairing and replacing bad components are clear and that maintenance personnel are trained to improve maintainability and reduce human errors and good spare parts inventory management on site.
B | SIL PERFORMANCE WITH EXTENDED MAINTENANCE/TEST INTERVAL
| PHM ESD reliability data calculations have been performed in order to verify the SIL classification when changing the ESD1 test-interval for from 1Y to 2Y. Result on proposed 2Y ESD1 test for SNB and SNPS paltform | [9 empty] | FAVOURABLE
Note: After implementing the 2Y ESD1 test strategy it is of the utmost importance to review/analyse the result of critical SDV & ESD1 test periodically (i.e. Annually) in order to verify if SIL level is still maintained!
C | Request for Derogation to be prepared and issued for management validation | [9 empty] | YES
2024-01-02
|  |  | Toni Harlan |  |  | Agus Dwi Heriyanto
|  | Date / version | Document responsible |  |  | Discipline responsible